Drinking Water Quality and Compliance

Annual Notice to Consumers – Town of Bruno 2025
Introduction

The Water Security Agency and the Ministry of Environment requires that at least once each year waterworks owners provide notification to consumers of the quality of water produced and supplied as well as information on the performance of the waterworks in submitting samples as required by a Minister’s Order or Permit to Operate a waterworks.  The following is a summary of the Town of Bruno water quality and sample submission compliance record for the 2025 calendar year.  This report was completed April 23rd, 2026.    Readers should refer to Water Security Agency’s Municipal Drinking Water Quality Monitoring Guidelines, June 2015, EPB 502 for more information on minimum sample submission requirements and the meaning of type of sample.  Permit requirements for a specific waterworks may require more sampling than outlined in the department’s monitoring guidelines.  If consumers need more information on the nature and significance of specific water tests, for example, “what is the significance of Selenium in a water supply”, more detailed information is available from:  http://www.hc-sc.gc.ca/ewh-semt/pubs/water-eau/index_e.html 
.

Water Quality Standards 

Bacteriological Quality



Regular Samples
Regular Samples
  # of Positive Regular

Parameter/Location
Limit


Required

Submitted
  Submitted (%)

Total Coliform 

0 Organisms/100 mL
52

52


0

E. coli


0 Organisms/100 mL
52

52


0
Background Bacteria
Less than 200/100 mL
______________
_______________  __________________
Water Disinfection – 

Chlorine Residual in Distribution System for Test Results Submitted with Bacteriological Samples


Minimum
Total Chlorine
Free Chlorine
# Tests
# Tests
# Adequate

Parameter
Limit
Residual Range
Residual Range
Required
Submitted
Chlorine (%)
Chlorine
0.1 mg/L free OR


Residual
0.5 mg/L total
.43          1.06
.35       .81
53
53

100%

Water Disinfection - Free Chlorine Residual for Water Entering Distribution System from Waterworks Records-From Water Treatment Plant Records



Test Level
# Tests                # Tests Not Meeting

Parameter
Limit (mg/L)
Range
Performed          Requirements

Free Chlorine Residual
at least 0.1
.44-.93
365                        0

A minimum of 0.1 milligrams per litre (mg/L) free chlorine residual is required for water entering the distribution system.  Tests are normally performed on a daily basis by the waterworks operator and are to be recorded in operation records.  This data includes the number of free chlorine residual tests performed, the overall range of free chlorine residual (highest and lowest recorded values) and the number of tests and percentage of results not meeting the minimum requirement of 0.1 mg/L free chlorine residual.

Turbidity – From Water Treatment Plant Records

Parameter
Limit
Test Level
# Tests Not Meeting
Maximum
# Tests           # Tests

# Tests


(NTU) 
Range
Requirements
Turbidity (NTU)
Required        Performed
Performed

Turbidity
1.00    .12  
.30
0
.30
365                      365

Chemical – Trihalomethanes (THMs)and Haloacetic Acids (HAAs)
Parameter
THMs

Sample
# Samples
#  Samples


Limit (mg/L)

Result (average) 
Required
Submitted

Trihalomethanes
0.1
.0527                      4 (1 every 3 months)
4
Haloacetic Acids
    0.08

   .0445                      4 (1 every 3 months)
       4
More information on water quality and sample submission performance may be obtained from:


Town of Bruno

Box 370, 601 Main Street


Bruno, Sask.   S0K 0S0


306-369-2514



E-mail address: office@brunosk.ca
[image: image1.jpg]Saskatchewan
Ministry of
Environment




                                                                          [image: image2.jpg]Water Securtty
Agency

O



                   

[image: image1.jpg][image: image2.jpg]